TRENDS IN TRANSFORMER LIFE-CYCLE MANAGEMENT ON-LOAD TAP-CHANGER AND TRANSFORMER ACCESSORIES

W. FLEISCHMANN, Maschinenfabrik Reinhausen GmbH – MR, Germany

ABSTRACT

Huge and outdated substations, various transformer brands and sizes, diverse tap-changer types, many transformer accessories and operational concepts, load behavior and ambient influences are – among others – a result of the enormous increase of energy demand within the last 30 years. In order to keep operation reliability and to integrate obsolete systems into modern substation concepts, it is of vital importance to develop Asset- Management and Maintenance Strategies.

Considering the installed base and technical data of transformers, a concept to calculate the importance and condition of the specific asset is necessary. Plant Maintenance management in consideration of importance and condition of the transformer is an efficient tool.

Key factors in accordance with operator standards have to be defined to review condition and importance of the particular transformer. Based on diagnostic measures and arithmetic systems, criteria with various weighting systems can be defined. The criteria illustrate a ranking of transformers. This ranking is a basis for Maintenance, availability, cost management and budget planning.

Uncountable transformer and OLTC test systems are available in the market. Reliability and accuracy of test systems are certainly the main criteria of test systems.  Having measurement values is essential for the diagnosis but the interpretation of these values and the resulting recommendation for Asset-Management is the most difficult and most important part of transformer diagnostic programs. It is essential to proceed on the basis of the diagnostics results, interpreting the respective actions in the right way.

1. Introduction

As a result of an enormous increase of energy demand the installed base of power transformers is growing faster than ever before. Strategic planning for transformer capacity expansion is an important chapter of the utility and industry sectors. As capacity planning for new transformers is - among other criteria - based on the already installed transformer capacity, it is even more important to consider modern strategies how to manage the existing assets.

Figure 1

Approx. number of installed transformers in Middle East

Source: MR Market Study

The bigger and older the entire transformer fleet becomes, the more important it is to consider Transformer Life-Cycle Management during the whole life span of the equipment. This paper puts a main focus on on-load tap-changer equipment and transformer accessories.

Figure 2

Risk of failure probability in % per year

Source: ABB TrafoAssetManagementTM

CIGRE WG 12-05 (1983) An internal survey on failures in large power transformers”

2. Asset-Management and Maintenance-Strategies for transformer OLTC and Accessories

Due to the enormous increase of the installed transformer base during the last 30 years, a clear strategy has to be developed how to manage the existing assets considering availability, reliability and cost efficiency.

Suitable Strategy means to detect any irregularities before they cause failures on the operational system.

Life-Cycle management starts with installation and commissioning of the transformer. Commissioning assures the proper function and will also provide a fingerprint (measurement values) for any further test and diagnostics.

The following steps of the commissioning procedure could be considered necessary for future Life-Cycle Management:

Transformer:

- Turn Ratio test

- Static Resistance Measurement

- Breakdown Voltage and Water Content of Transformer oil

On-Load Tap-Changer:

- Dynamic Resistance Measurement

- Breakdown Voltage and Water Content of OLTC Oil

- Electrical and mechanical test

Transformer Accessories:

- Verification of all Measurement Systems like OTI/WTI

- Verification of van control system

- Verification of protection systems

- Documentation of all above mentioned values

Every utility and transformer user should define a standard for the documentation of all assets including measured values and performed services.

2.1.  Maintenance Philosophies

The overall Asset-Management strategy is based on different service philosophies considering importance and reliability of the respective components. Transformer operators usually select and define a combination of the following philosophies.

Risk based / event based Maintenance

Any inspection, repair or Maintenance work will be carried out only after a failure occurs. Within this philosophy the failure indicates the necessity for further steps. No predictive Maintenance plan is available.

Risk based Maintenance is definitely considered as a wrong strategy.

Time based Maintenance / Predictive Maintenance

The Maintenance steps are carried out within fixed intervals, time frames and criteria indicated by the original manufacturers and the respective operating manuals of the equipment. This philosophy offers easy planning (shut down times, spare parts) and improves the condition of the equipment.

Condition based Maintenance

Any services and Maintenance work is carried out based on the condition of the equipment. The right component shall be maintained at the right time. Fixed parameters and conditions have to be defined and set as references. The work has to be carried out if the reference levels are reached or if one or more parameters indicate the need of Maintenance. Planning of shutdown time and spare part availability needs attention. Sensors, test procedures and monitoring systems are necessary in order to know the condition.

Preventive Maintenance

Finally, and considering all aspects and philosophies, any Asset-Management plan or Maintenance strategy should be preventive and assure the reliability and proper function of the overall equipment.

Figure 3

Theory of preventive Maintenance by Siemens TLMTM

NO Maintenance

(use of Maintenance-Free products)

If Maintenance-Free products are used for new projects or if Maintenance-Free products are installed as retrofit projects, then the Maintenance-Free strategy could be followed. The use of such Maintenance-Free products (e.g. Vacuum OLTC, Dehydrating Breather …) is part of modern Asset-Management strategies.

  - Modern Asset-Management Strategies include:

- Reliability Centered Maintenance

- Condition Assessment

- Strategy combined of time and condition based Maintenance

- Determination of the appropriate level of the necessary Maintenance

- Determination of the necessary task when to perform a Maintenance

- Training of Maintenance teams

- Replacement of components with longer Maintenance intervals

- End of life determination for assets

- Technically and economically optimized solutions for assets

3. Criteria – Condition Assessment

In some areas the capacity increase (installation of new transformers) was much more important / required than maintaining the existing assets. In such cases (lack of Maintenance and operating information) diagnostic tools are required in order to create a ranking and to know where to start.

In order to define an Asset-Management strategy or to combine the different Maintenance philosophies, a condition Assessment plan has to be developed.

For instance, integrated plant Maintenance covers the planning of required Maintenance measures for transformers (combination of the Maintenance philosophies) taking the following criteria into consideration:

Condition (examples)

- Age

- Number of operations

- Load factor

- Operational experience

- Noise level

- Annual operating hours

- Power transmission

- Diagnostic results

- Service and supply of spare parts

Importance (examples)

- Consequences of outages

- Number of substitute devices

- Investment cost

- Power conversion

- Voltage level

- Voltage quality

- Availability

- Etc.

Based on a calculation the importance and condition INDEX can be defined in accordance with the following example:

Figure 4

Transformer index

The evaluated index finally indicates the priority of Maintenance requirement for the assets in operation.

Figure 5

Classification of Assets

Source: BWK Magazine

4. Transformer Accessories and OLTC Diagnostics for Assessment purposes

As mentioned in chapter 3, among other criteria, diagnostic results are required in order to get a ranking about the condition of outdated transformers.

Beside diagnostics for the transformer itself, diagnostics in order to know the condition of the accessories and the tap-changer have to be carried out, too.

After any diagnostics, qualified partners with long term experience are necessary in order to develop an expertise and a respective Maintenance-strategy. It is essential to evaluate all diagnostic results in a professional way and to define a guide which preventive action/ Maintenance need to be done in accordance with the respective time intervals.

Any diagnostic measure and Assessment procedure will NOT replace Maintenance work.

The following steps should be considered for transformer accessories and OLTC Assessment.

- Documentation of design data / technical data and serial numbers of transformer and tap-changer

- Documentation of type and technical data of the transformer accessories

- Service history

- Visual inspection of whole system (damages / leakages etc.)

- Electrical Measurements (Dynamic Resistance Measurement)

- Standard Transformer Oil Tests (DGA, Breakdown Voltage, Moisture, Furanic Analysis)

- Standard OLTC Oil Test (Breakdown Voltage, Moisture)

- Functional test accessories (calibration bath, current simulator…)

5.  Modernization of Power Transformers

Professional routine Maintenance and Modernization of transformers is a significant element during the lifecycle of transformers.

Beside routine Maintenance requirements, criteria for transformer Modernization are:

- General overhaul of a transformer for another lifespan of 25 years and longer

- Aging of the transformer components

- End of life time of transformer components or breakdown of components

- Technical development and product innovation, e.g. new AVR with a new communication system

- The need for increased transformer availability

- Operating the transformer with a higher load

- Limited availability of spare parts

- Technical and economical evaluation between Modernization or replacement by a new asset

Transformer Modernization needs proper planning and preparation to assure minimum outage time and maximum cost efficiency

Figure 6

Example for time schedule

Planning and preparation:

- Documentation system

- Identification of Scope of Work

- Description of individual tasks

- Detailed time schedule for all phases

- Outage time / outage scenario

- Determination of appropriate Maintenance tasks

- Required sources (personnel, tools, spare parts, etc.)

- Quality control

- Health and safety measures

- Cost breakdown

- Training of operator personnel

Another important decision is if the Modernization shall take place on-site or in a workshop. Size of the transformer, scope of work and capability of the transformer specialist company are the main reasons which influence this decision.

5.1  Components for transformer Modernization and benefits

On-Load Tap-Changers

- Load increase

- Upgrade to Maintenance-Free equipment (vacuum technology)

- Reliability of a main component

- Change from earlier bolt-on systems to modern in-tank systems

Figure7

OLTC replacement

Motor-Drive Units

- Reliable remote operation

- Transparent and modular design

- Integration into modern communication systems

- Maintenance-Free & protected

Figure 8

Motor-drive unit replacement

Gauges and Measurement Systems

- Calibration & Maintenance-Free

- Precise and reliable technology

- Advanced cooling control

- Communication with modern control system

Figure 9

Temperature Control Systems

Protection system

- Approved protection, maximum safety

- No false alarms

- Optimal characteristics / setting options

- Test options

Figure 10

Leaking PRD

Voltage Regulators including Monitoring functions

- Integration into modern control system (IEC61850)

- Individual hardware configuration for flexible functions

- Reliable and most efficient operation of the transformer system

Cost saving due to intelligent regulation

1980                                           2012

Figure 11

Voltage regulators

Dehydrating Breather Systems

- More efficient dehydration

- Extension of transformer life

- Maintenance-Free system; increased operating reliability

- Much less operating costs

Figure 12

Dehydrating breathers

On-line Oil Filter Systems for conventional Tap-Changers operating in oil

- Efficient oil cleaning

- Less carbonization and moisture

- Reliable operating system

- Pressure switch and manometer

Figure 13

Oil filter systems for OLTC

CONCLUSION

Professional Maintenance and Modernization of transformers is a significant element in the lifecycle of transformers. Various reasons can be determined during transformer Assessment. Modifications based on the latest technical condition put the transformers on an up-to-date technical level so that they can be easily integrated in all modern substation networks. Such modified and upgraded transformers work reliably and efficiently like new systems.

Operation and Maintenance departments should invite experienced service partners in order to evaluate a clear and tailor-made Asset-Management Strategy.

LIST OF REFERENCES

- CIGRE Working Group 2.34 – Guide for Transformer Maintenance

- ABB Presentation TrafoAssetManagementTM Proactive Services

- Siemens TLMTM http://www.siemens.com/energy/TLM

- Maschinenfabrik Reinhausen GmbH, Johannes Gebauer, Servicekonzept an Stufenschaltern –   Erfahrungen aus der Praxis

- Maschinenfabrik Reinhausen GmbH, Johannes Gebauer, Tailor Made Solutions for Transformer, Modernization

Werner Fleischmann, Maschinenfabrik Reinhausen GmbH – MR, Falkensteinstrasse 8, 93059 Regensburg, GERMANY